| Legionnaire’s Disease Risk Assessment |  |  |
| --- | --- | --- |
| When you do the risk assessment, consider the following: A visual inspection of the installations and fittings should be carried out, bearing the points below in mind. As many of the practical tips as possible should be put in place. It may be appropriate to check the temperature of the water in pipes, cold water cisterns, hot water storage vessels and the discharge from taps. Water sampling and analysis may be considered necessary if risks are identified. Lastly, your assessment should be reviewed periodically, particularly if any factors change. |  |  |
| Risk Factor | Advice for control | Result of check and risk level – low/acceptable/high. Actions to be taken where risks identified. |
| Could cold water in tanks or pipework be at above 20°C ? | Ensure cold water is stored at a temperature as low as possible, at least below 20°C. Insulating pipework may help. | Run cold taps to test water temperature. |
| Could hot water be stored below 45°C ? | To prevent Legionella growth, hot water needs to be maintained above 55°C. To achieve this, hot water tanks should be set to store the water at above 60°C. Insulating pipework may also help keep water hot until it is used. (beware the risk of scalding however, possibly by placing mixer valves at taps) | Does the property have a hot water tank or is it run from a combi boiler? If combi then no hot water is stored so risk factor is not applicable. |
| Are there areas where stagnant water occurs (deadlegs), eg pipes to a washing machine that is no longer used? | Ensure water cannot stagnate anywhere in the system, remove redundant pipework or appliances. |  |
| Are there infrequently used outlets, eg showers, taps? | If so, have a system for periodically running the taps/showers in these units. | Run taps for 2 minutes to clear system backlog. |
| Have any rooms or properties been vacant for some time as the water will have been stagnant in the pipes. | Again, have a system for periodically running the taps / showers in unoccupied rooms. | Run taps for 2 minutes to clear system backlog. |
| Is there debris in the system, such as rust, sludge or scale (often a problem in old metal cisterns), that could provide food for growing legionella? | Check periodically and clean out when necessary. Consider modernising old tanks and cisterns etc. |  |
| Are any tanks covered to prevent access to mice, birds, insects and general dirt and debris. | All water cisterns should be covered, insulated, clean and free of debris. Covering will go a long way to ensure this. |  |
| Is backflow possible from fittings or appliances into pipework connected to mains or other fittings or appliances? | Particularly consider hoses attached to external taps. Being outside, they are more likely to suffer contamination, which could then be drawn into the property. Ask tenants not to leave hoses attached when not in use. |  |
| Is there a cross-connection between pipes conveying water supplied for tenants direct use with pipes conveying water from some other source? | Follow pipes to track the flow of water, particularly that people will have direct contact with. |  |
| Are any of your employees, tenants, visitors etc. vulnerable to infection, e.g. older people, those already ill? | You should advise tenants about the risks, the control measures you are taking and the precautions they can take, such as flushing through showers following a period of non-use. | Issue RLA advice sheet for tenants. Note date of issue. |
| Are you about to carry out maintenance to or renovation of old systems or units that have been vacant for some time? | You should advise maintenance staff working on the system about the risks and how to minimise them. | Issue Government guidance notes HSG274 Part 2 Published 2014, a copy of the latest RA and ask for completion of new RA re. completed works. |